## All Points
REST Name (VSN700) | REST Name (VSN300) | SunSpec Normalized Name | HA Entity Name | In /livedata | In /feeds | SunSpec Model | Category | Units | State Class | Device Class | Available in Modbus
Pgrid | m103_1_W | W | W | ✓ | ✓ | M103 | Inverter | W | measurement | power | YES
Igrid | m103_1_A | A | A | ✓ |  | M103 | Inverter | A | measurement | current | YES
Vgrid | m103_1_PhVphA | PhVphA | PhVphA | ✓ |  | M103 | Inverter | V | measurement | voltage | YES
Fgrid | m103_1_Hz | Hz | Hz | ✓ |  | M103 | Inverter | Hz | measurement | frequency | YES
cosPhi | m103_1_PF | PF | PF | ✓ | ✓ | M103 | Inverter | % | measurement | power_factor | YES
Qgrid | m103_1_VAR | VAR | VAR | ✓ | ✓ | M103 | Inverter | var | measurement | reactive_power | YES
Pin | m103_1_DCW | DCW | DCW | ✓ | ✓ | M103 | Inverter | W | measurement | power | YES
ETotal | m103_1_WH | WH | WH | ✓ | ✓ | M103 | Inverter | Wh | total_increasing | energy | YES
Ein | m103_1_WH | WH | WH | ✓ | ✓ | M103 | Inverter | Wh | total_increasing | energy | YES
TempInv | m103_1_TmpOt | TmpOt | TmpOt | ✓ |  | M103 | Inverter | °C | measurement | temperature | YES
Temp1 | m103_1_TmpCab | TmpCab | TmpCab | ✓ | ✓ | M103 | Inverter | °C | measurement | temperature | YES
WRtg | m120_1_WRtg | WRtg | WRtg | ✓ |  | M120 | Inverter | W |  | power | YES
Iin1 | m160_1_DCA_1 | DCA_1 | DCA_1 | ✓ |  | M160 | MPPT | A | measurement | current | YES
Vin1 | m160_1_DCV_1 | DCV_1 | DCV_1 | ✓ |  | M160 | MPPT | V | measurement | voltage | YES
Pin1 | m160_1_DCW_1 | DCW_1 | DCW_1 | ✓ | ✓ | M160 | MPPT | W | measurement | power | YES
Iin2 | m160_1_DCA_2 | DCA_2 | DCA_2 | ✓ |  | M160 | MPPT | A | measurement | current | YES
Vin2 | m160_1_DCV_2 | DCV_2 | DCV_2 | ✓ |  | M160 | MPPT | V | measurement | voltage | YES
Pin2 | m160_1_DCW_2 | DCW_2 | DCW_2 | ✓ | ✓ | M160 | MPPT | W | measurement | power | YES
TSoc | m124_1_ChaState | ChaState | ChaState | ✓ |  | M124 | Battery | % | measurement | battery | YES
PbaT | m124_1_InWRte | InWRte | InWRte | ✓ | ✓ | M124 | Battery | W | measurement | power | YES
Soc | m802_1_SoC | SoC | SoC | ✓ |  | M802 | Battery | % | measurement | battery | YES
Soh | m802_1_SoH | SoH | SoH | ✓ |  | M802 | Battery | % | measurement |  | YES
Vba | m802_1_V | V | V | ✓ |  | M802 | Battery | V | measurement | voltage | YES
Iba | m802_1_A | A | A | ✓ |  | M802 | Battery | A | measurement | current | YES
Pba | m802_1_W | W | W | ✓ |  | M802 | Battery | W | measurement | power | YES
Tba | m802_1_Tmp | Tmp | Tmp | ✓ |  | M802 | Battery | °C | measurement | temperature | YES
CycleNum | m802_1_NCyc | NCyc | NCyc | ✓ |  | M802 | Battery |  | total |  | YES
VcMax | m802_1_CellVMax | CellVMax | CellVMax | ✓ |  | M802 | Battery | V | measurement | voltage | YES
VcMin | m802_1_CellVMin | CellVMin | CellVMin | ✓ |  | M802 | Battery | V | measurement | voltage | YES
TcMax | m802_1_CellTmpMax | CellTmpMax | CellTmpMax | ✓ |  | M802 | Battery | °C | measurement | temperature | YES
TcMin | m802_1_CellTmpMin | CellTmpMin | CellTmpMin | ✓ |  | M802 | Battery | °C | measurement | temperature | YES
PCh | m802_1_AChaMax | AChaMax | AChaMax | ✓ |  | M802 | Battery | A | measurement | current | YES
PDh | m802_1_ADisChaMax | ADisChaMax | ADisChaMax | ✓ |  | M802 | Battery | A | measurement | current | YES
Fcc | m802_1_AHRtg | AHRtg | AHRtg | ✓ |  | M802 | Battery | Ah |  |  | YES
VgridL1_N | m101_1_PhVphA | PhVphA | PhVphA | ✓ |  | M101 | Inverter | V | measurement | voltage | YES
VgridL2_N | m101_1_PhVphB | PhVphB | PhVphB | ✓ |  | M101 | Inverter | V | measurement | voltage | YES
SplitPhase | N/A | SplitPhase | SplitPhase | ✓ |  | M101 | Inverter |  |  |  | YES
MeterPgrid_Tot | m203_1_W | W | W | ✓ | ✓ | M203 | Meter | W | measurement | power | YES
MeterPgrid_L1 | m203_1_WphA | WphA | WphA | ✓ |  | M203 | Meter | W | measurement | power | YES
MeterPgrid_L2 | m203_1_WphB | WphB | WphB | ✓ |  | M203 | Meter | W | measurement | power | YES
MeterPgrid_L3 | m203_1_WphC | WphC | WphC | ✓ |  | M203 | Meter | W | measurement | power | YES
MeterVgrid_L1 | m203_1_PhVphA | PhVphA | PhVphA | ✓ |  | M203 | Meter | V | measurement | voltage | YES
MeterVgrid_L2 | m203_1_PhVphB | PhVphB | PhVphB | ✓ |  | M203 | Meter | V | measurement | voltage | YES
MeterVgrid_L3 | m203_1_PhVphC | PhVphC | PhVphC | ✓ |  | M203 | Meter | V | measurement | voltage | YES
MeterIgrid_L1 | m203_1_AphA | AphA | AphA | ✓ |  | M203 | Meter | A | measurement | current | YES
MeterIgrid_L2 | m203_1_AphB | AphB | AphB | ✓ |  | M203 | Meter | A | measurement | current | YES
MeterIgrid_L3 | m203_1_AphC | AphC | AphC | ✓ |  | M203 | Meter | A | measurement | current | YES
MeterQgrid_Tot | m203_1_VAR | VAR | VAR | ✓ |  | M203 | Meter | var | measurement | reactive_power | YES
MeterQgrid_L1 | m203_1_VARphA | VARphA | VARphA | ✓ |  | M203 | Meter | var | measurement | reactive_power | YES
MeterQgrid_L2 | m203_1_VARphB | VARphB | VARphB | ✓ |  | M203 | Meter | var | measurement | reactive_power | YES
MeterQgrid_L3 | m203_1_VARphC | VARphC | VARphC | ✓ |  | M203 | Meter | var | measurement | reactive_power | YES
MeterFgrid | m203_1_Hz | Hz | Hz | ✓ |  | M203 | Meter | Hz | measurement | frequency | YES
EGridImport | m203_1_TotWhImp | TotWhImp | TotWhImp | ✓ | ✓ | M203 | Meter | Wh | total_increasing | energy | YES
EGridExport | m203_1_TotWhExp | TotWhExp | TotWhExp | ✓ | ✓ | M203 | Meter | Wh | total_increasing | energy | YES
E0_1Y | m64061_1_E0_1Y | abb_E0_1Y | abb_E0_1Y | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E0_30D | m64061_1_E0_30D | abb_E0_30D | abb_E0_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E0_7D | m64061_1_E0_7D | abb_E0_7D | abb_E0_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E0_runtime | N/A | abb_E0_runtime | abb_E0_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E15_30D | m64061_1_E15_30D | abb_E15_30D | abb_E15_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E15_7D | m64061_1_E15_7D | abb_E15_7D | abb_E15_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E15_runtime | N/A | abb_E15_runtime | abb_E15_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E1_30D | m64061_1_E1_30D | abb_E1_30D | abb_E1_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E1_7D | m64061_1_E1_7D | abb_E1_7D | abb_E1_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E1_runtime | N/A | abb_E1_runtime | abb_E1_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E2_30D | m64061_1_E2_30D | abb_E2_30D | abb_E2_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E2_7D | m64061_1_E2_7D | abb_E2_7D | abb_E2_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E2_runtime | N/A | abb_E2_runtime | abb_E2_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E3_30D | m64061_1_E3_30D | abb_E3_30D | abb_E3_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E3_7D | m64061_1_E3_7D | abb_E3_7D | abb_E3_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E3_runtime | N/A | abb_E3_runtime | abb_E3_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E4_30D | m64061_1_E4_30D | abb_E4_30D | abb_E4_30D | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E4_7D | m64061_1_E4_7D | abb_E4_7D | abb_E4_7D | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E4_runtime | N/A | abb_E4_runtime | abb_E4_runtime | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E5_30D | m64061_1_E5_30D | abb_E5_30D | abb_E5_30D | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E5_7D | m64061_1_E5_7D | abb_E5_7D | abb_E5_7D | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E5_runtime | N/A | abb_E5_runtime | abb_E5_runtime | ✓ |  | M64061 | Energy Counter | Wh | total | energy | MAYBE
E6_30D | m64061_1_E6_30D | abb_E6_30D | abb_E6_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E6_7D | m64061_1_E6_7D | abb_E6_7D | abb_E6_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E6_runtime | N/A | abb_E6_runtime | abb_E6_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E7_30D | m64061_1_E7_30D | abb_E7_30D | abb_E7_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E7_7D | m64061_1_E7_7D | abb_E7_7D | abb_E7_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E7_runtime | N/A | abb_E7_runtime | abb_E7_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E8_30D | m64061_1_E8_30D | abb_E8_30D | abb_E8_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E8_7D | m64061_1_E8_7D | abb_E8_7D | abb_E8_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
E8_runtime | N/A | abb_E8_runtime | abb_E8_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ECharge_30D | m64061_1_ECharge_30D | abb_ECharge_30D | abb_ECharge_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ECharge_7D | m64061_1_ECharge_7D | abb_ECharge_7D | abb_ECharge_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ECharge_runtime | N/A | abb_ECharge_runtime | abb_ECharge_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
EDischarge_30D | m64061_1_EDischarge_30D | abb_EDischarge_30D | abb_EDischarge_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
EDischarge_7D | m64061_1_EDischarge_7D | abb_EDischarge_7D | abb_EDischarge_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
EDischarge_runtime | N/A | abb_EDischarge_runtime | abb_EDischarge_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotCharge_30D | m64061_1_ETotCharge_30D | abb_ETotCharge_30D | abb_ETotCharge_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotCharge_7D | m64061_1_ETotCharge_7D | abb_ETotCharge_7D | abb_ETotCharge_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotCharge_runtime | N/A | abb_ETotCharge_runtime | abb_ETotCharge_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotDischarge_30D | m64061_1_ETotDischarge_30D | abb_ETotDischarge_30D | abb_ETotDischarge_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotDischarge_7D | m64061_1_ETotDischarge_7D | abb_ETotDischarge_7D | abb_ETotDischarge_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
ETotDischarge_runtime | N/A | abb_ETotDischarge_runtime | abb_ETotDischarge_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
Ein_30D | m64061_1_Ein_30D | abb_Ein_30D | abb_Ein_30D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
Ein_7D | m64061_1_Ein_7D | abb_Ein_7D | abb_Ein_7D | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
Ein_runtime | N/A | abb_Ein_runtime | abb_Ein_runtime | ✓ | ✓ | M64061 | Energy Counter | Wh | total | energy | MAYBE
AlarmState | m64061_1_AlarmState | abb_AlarmState | abb_AlarmState | ✓ |  | M64061 | Status |  | measurement |  | MAYBE
CountryStd | m64061_1_CountryStd | abb_CountryStd | abb_CountryStd | ✓ |  | M64061 | Diagnostic |  | measurement |  | MAYBE
DC1State | m64061_1_DC1State | abb_DC1State | abb_DC1State | ✓ |  | M64061 | Status |  | measurement |  | MAYBE
DC2State | m64061_1_DC2State | abb_DC2State | abb_DC2State | ✓ |  | M64061 | Status |  | measurement |  | MAYBE
GlobState | m64061_1_GlobState | abb_GlobState | abb_GlobState | ✓ |  | M64061 | Status |  | measurement |  | MAYBE
IleakDC | m64061_1_IleakDC | abb_IleakDC | abb_IleakDC | ✓ |  | M64061 | Isolation | A | measurement |  | MAYBE
IleakInv | m64061_1_IleakInv | abb_IleakInv | abb_IleakInv | ✓ |  | M64061 | Isolation | A | measurement |  | MAYBE
InvState | m64061_1_InvState | abb_InvState | abb_InvState | ✓ |  | M64061 | Status |  | measurement |  | MAYBE
Ppeak | m64061_1_Ppeak | abb_Ppeak | abb_Ppeak | ✓ |  | M64061 | Diagnostic |  | measurement |  | MAYBE
Riso | m64061_1_Riso | abb_Riso | abb_Riso | ✓ |  | M64061 | Isolation |  | measurement |  | MAYBE
SysTime | m64061_1_SysTime | abb_SysTime | abb_SysTime | ✓ |  | M64061 | Diagnostic |  | measurement |  | MAYBE
TempBst | m64061_1_TempBst | abb_TempBst | abb_TempBst | ✓ |  | M64061 | Diagnostic |  | measurement |  | MAYBE
VBulk | m64061_1_VBulk | abb_VBulk | abb_VBulk | ✓ |  | M64061 | Isolation | V | measurement | voltage | MAYBE
VBulkMid | m64061_1_VBulkMid | abb_VBulkMid | abb_VBulkMid | ✓ |  | M64061 | Isolation | V | measurement | voltage | MAYBE
Vgnd | m64061_1_Vgnd | abb_Vgnd | abb_Vgnd | ✓ |  | M64061 | Isolation | V | measurement | voltage | MAYBE
BattExtCtrlEna | N/A | abb_BattExtCtrlEna | abb_BattExtCtrlEna | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
BattExtCtrlState | N/A | abb_BattExtCtrlState | abb_BattExtCtrlState | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
BattNum | N/A | abb_BattNum | abb_BattNum | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
BatteryMode | N/A | abb_BatteryMode | abb_BatteryMode | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
Chc | N/A | abb_Chc | abb_Chc | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
ClockState | N/A | abb_ClockState | abb_ClockState | ✓ |  | ABB Proprietary | Other |  | measurement |  | NO
CommissioningFreeze | N/A | abb_CommissioningFreeze | abb_CommissioningFreeze | ✓ |  | ABB Proprietary | Other |  | measurement |  | NO
DI0_mode | N/A | abb_DI0_mode | abb_DI0_mode | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
DI1_mode | N/A | abb_DI1_mode | abb_DI1_mode | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
DI_status | N/A | abb_DI_status | abb_DI_status | ✓ |  | ABB Proprietary | Other |  | measurement |  | NO
DetectedBatteryNumber | N/A | abb_DetectedBatteryNumber | abb_DetectedBatteryNumber | ✓ |  | ABB Proprietary | Other |  | measurement |  | NO
Dhc | N/A | abb_Dhc | abb_Dhc | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
DynamicFeedInCtrl | N/A | abb_DynamicFeedInCtrl | abb_DynamicFeedInCtrl | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
EBackup | N/A | abb_EBackup | abb_EBackup | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
ECharge | N/A | abb_ECharge | abb_ECharge | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
ECt | N/A | abb_ECt | abb_ECt | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
EDischarge | N/A | abb_EDischarge | abb_EDischarge | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
EDt | N/A | abb_EDt | abb_EDt | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
ETotalAbsorbed | N/A | abb_ETotalAbsorbed | abb_ETotalAbsorbed | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
ETotalApparent | N/A | abb_ETotalApparent | abb_ETotalApparent | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
Ein1 | N/A | abb_Ein1 | abb_Ein1 | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
Ein2 | N/A | abb_Ein2 | abb_Ein2 | ✓ |  | ABB Proprietary | Energy Counter |  | total_increasing |  | NO
EnergyPolicy | N/A | abb_EnergyPolicy | abb_EnergyPolicy | ✓ |  | ABB Proprietary | Battery Ext |  | total_increasing |  | NO
FRT_state | N/A | abb_FRT_state | abb_FRT_state | ✓ |  | ABB Proprietary | Other |  | measurement |  | NO
Fan1rpm | N/A | abb_Fan1rpm | abb_Fan1rpm | ✓ |  | ABB Proprietary | System Info |  | measurement |  | NO
Fan2rpm | N/A | abb_Fan2rpm | abb_Fan2rpm | ✓ |  | ABB Proprietary | System Info |  | measurement |  | NO
HouseIgrid_L1 | N/A | abb_HouseIgrid_L1 | abb_HouseIgrid_L1 | ✓ |  | ABB Proprietary | House Meter | A | measurement | current | NO
HouseIgrid_L2 | N/A | abb_HouseIgrid_L2 | abb_HouseIgrid_L2 | ✓ |  | ABB Proprietary | House Meter | A | measurement | current | NO
HouseIgrid_L3 | N/A | abb_HouseIgrid_L3 | abb_HouseIgrid_L3 | ✓ |  | ABB Proprietary | House Meter | A | measurement | current | NO
HousePInverter | N/A | abb_HousePInverter | abb_HousePInverter | ✓ | ✓ | ABB Proprietary | House Meter |  | measurement |  | NO
HousePgrid_L1 | N/A | abb_HousePgrid_L1 | abb_HousePgrid_L1 | ✓ |  | ABB Proprietary | House Meter | W | measurement | power | NO
HousePgrid_L2 | N/A | abb_HousePgrid_L2 | abb_HousePgrid_L2 | ✓ |  | ABB Proprietary | House Meter | W | measurement | power | NO
HousePgrid_L3 | N/A | abb_HousePgrid_L3 | abb_HousePgrid_L3 | ✓ |  | ABB Proprietary | House Meter | W | measurement | power | NO
HousePgrid_Tot | N/A | abb_HousePgrid_Tot | abb_HousePgrid_Tot | ✓ | ✓ | ABB Proprietary | House Meter | W | measurement | power | NO
InputMode | N/A | abb_InputMode | abb_InputMode | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
NumOfMPPT | N/A | abb_NumOfMPPT | abb_NumOfMPPT | ✓ |  | ABB Proprietary | System Info |  | measurement |  | NO
PACDeratingFlags | N/A | abb_PACDeratingFlags | abb_PACDeratingFlags | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
PacStandAlone | N/A | abb_PacStandAlone | abb_PacStandAlone | ✓ |  | ABB Proprietary | Hybrid |  | measurement |  | NO
PacTogrid | N/A | abb_PacTogrid | abb_PacTogrid | ✓ |  | ABB Proprietary | Hybrid | W | measurement | power | NO
QACDeratingFlags | N/A | abb_QACDeratingFlags | abb_QACDeratingFlags | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
SACDeratingFlags | N/A | abb_SACDeratingFlags | abb_SACDeratingFlags | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
ShU | N/A | abb_ShU | abb_ShU | ✓ |  | ABB Proprietary | Battery Ext |  | measurement |  | NO
WarningFlags | N/A | abb_WarningFlags | abb_WarningFlags | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
gridExtCtrlEna | N/A | abb_gridExtCtrlEna | abb_gridExtCtrlEna | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
gridExtCtrlState | N/A | abb_gridExtCtrlState | abb_gridExtCtrlState | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
m126Mod_Ena | N/A | abb_m126Mod_Ena | abb_m126Mod_Ena | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO
m132Mod_Ena | N/A | abb_m132Mod_Ena | abb_m132Mod_Ena | ✓ |  | ABB Proprietary | Control |  | measurement |  | NO

## Summary
Category | Count
Total Points | 162
Standard SunSpec (Both protocols) | 54
M64061 (Maybe in Modbus) | 61
ABB Proprietary (REST only) | 47
In /livedata | 162
In /feeds | 55