## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4a based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2019-12-06 09:38:14
Manufacturer Name | FIMER
Product Name | REACT2
Product Models | REACT2-UNO-3.6-TL, REACT2-UNO-5.0-TL
Product Description | Single Phase String Inverter with Storage

## Versioning
Version | Change Log | Date of Change | Min. Ref. FW version Inverter | Min. Ref. FW version Logger
1 | - First version | 2019-12-06 | 1941E | 0.4.15
2 | - 65232 map has been added | 21/12/2020 | 2022C | 0.6.7
3 | - Changed manufacturer to FIMER | 2021-09-07 00:53 | 2022C | 0.6.7
4
5
6
7
8
9
10
11
12
13
14
15
16

## 1
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40002 | ID | Common |  | uint16 |  |  | 1 |  |  | Include this model for single phase inverter monitoring
40003 | L |  |  | uint16 |  |  | 66 |  |  | Model Length
40004 | Mn | Manufacturer |  | string |  |  | FIMER |  | R | Well known value registered with SunSpec for compliance
40020 | Md | Model |  | string |  |  | -3P81- |  | R | Manufacturer specific value (32 chars) | Provided Md string is the part number of the specific model: -3P88- = REACT2-UNO-3.6-TL -3P81- = REACT2-UNO-5.0-TL
40036 | Opt | Options |  | string |  |  | 0x0DED/0xFF6A/ |  | R | Manufacturer specific value (16 chars) | Provided Opt string is formatted as a list of string fields separated by '/' character [Field 1/Field 2/]: - Field 1: Model identifier formatted as [Model ID + Family ID] where Model ID is the identifier for the inverter type and Family ID is the identifier for the inverter family. The IDs uniquely represent an inverter model. If one of the ID bytes is not-printable then they will be both presented as hexadecimal values preceded by "0x" string; if both ID bytes are printable then they will be presented with the corresponding ASCII characters. IDs pair are: 0x0EED for REACT2-UNO-3.6-TL (Model ID = 0D, Family ID = ED) 0x0DED for REACT2-UNO-5.0-TL (Model ID = 0D, Family ID = ED) - Field 2: reserved for internal use
40044 | Vr | Version |  | string |  |  | 1926A |  | R | Manufacturer specific value (16 chars) | Provided SW release version string is formatted as [Y + WY + DW] where Y is the release year (format YY), WY is the release week of the year (format WW) and DW is the release day of the week (encoded as a single ASCII character starting from 'A' which is associated to Monday) Example: 1801C is the encoding number that define the firmware released Wednesday on the first week of 2018
40052 | Number | Serial |  | string |  |  | 111111-3P81-3118 |  | R | Manufacturer specific value (32 chars) | Provided serial number string is formatted as [SN + PN + WY] where SN is the internal serial number of the unit, PN is the internal part number of the unit and WY is the manufacturing week/year date expressed in WWYY format. The inverter label and official serial number is composed by the following format [YW+SN]. Example: the following register value 001001-3P20-0517 is associated as SN=001001; PN = -3P20-; W=05; SN=17. The label serial number is 1705001001.
40068 | Address | Device |  | uint16 |  |  | 1 |  | RW | Modbus device address
40069 | Pad | Pad |  | pad |  |  |  |  | R | Force even alignment

## 101
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40070 | ID | Inverter (Three Phase) |  | uint16 |  |  | 101 |  |  | Include this model for single phase inverter monitoring
40071 | L |  |  | uint16 |  |  | 50 |  |  | Model Length
40072 | A | Amps |  | uint16 | A | A_SF | supported |  | R | AC Current
40073 | AphA | Amps PhaseA |  | uint16 | A | A_SF | supported |  | R | Phase A Current
40074 | AphB | Amps PhaseB |  | uint16 | A | A_SF | unimplemented |  | R | Phase B Current
40075 | AphC | Amps PhaseC |  | uint16 | A | A_SF | unimplemented |  | R | Phase C Current
40076 |  | A_SF |  | sunssf |  |  | -1 |  | R
40077 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage AB
40078 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage BC
40079 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage CA
40080 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AN
40081 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage BN
40082 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage CN
40083 |  | V_SF |  | sunssf |  |  | -1 |  | R
40084 | W | Watts |  | int16 | W | W_SF | supported |  | R | AC Power
40085 |  | W_SF |  | sunssf |  |  | 1 |  | R
40086 |  | Hz |  | uint16 | Hz | Hz_SF | supported |  | R | Line Frequency
40087 |  | Hz_SF |  | sunssf |  |  | -2 |  | R
40088 |  | VA |  | int16 | VA | VA_SF | supported |  | R | AC Apparent Power
40089 |  | VA_SF |  | sunssf |  |  | 1 |  | R
40090 |  | Var |  | int16 | var | VAr_SF | supported |  | R | AC Reactive Power
40091 |  | VAr_SF |  | sunssf |  |  | 1 |  | R
40092 |  | PF |  | int16 | Pct | PF_SF | supported |  | R | AC Power Factor | The PF sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40093 |  | PF_SF |  | sunssf |  |  | -4 |  | R
40094 | WH | WattHours |  | acc32 | Wh | WH_SF | supported |  | R | AC Energy | Total Energy. Provided also with model 122 (ActWh)
40096 |  | WH_SF |  | sunssf |  |  | 1 |  | R
40097 | DCA | DC Amps |  | uint16 | A | DCA_SF | supported |  | R | DC Current
40098 |  | DCA_SF |  | sunssf |  |  | -1 |  | R
40099 | DCV | DC Voltage |  | uint16 | V | DCV_SF | unimplemented |  | R | DC Voltage | For this product the DC voltage is not provided with model 101 but using model 160.
40100 |  | DCV_SF |  | sunssf |  |  | unimplemented |  | R
40101 | DCW | DC Watts |  | int16 | W | DCW_SF | supported |  | R | DC Power
40102 |  | DCW_SF |  | sunssf |  |  | 1 |  | R
40103 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | supported |  | R | Cabinet Temperature | This measure is implemented as internal enclouser temperature.
40104 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | supported |  | R | Heat Sink Temperature | This measure is implemented as DC/AC (inverter) stage heatsink temperature.
40105 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | unimplemented |  | R | Transformer Temperature
40106 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | supported |  | R | Other Temperature | This measure is implemented as DC/DC (booster) stage heatsink temperature.
40107 |  | Tmp_SF |  | sunssf |  |  | -1 |  | R
40108 | St | Operating State |  | enum16 |  |  | supported |  | R | Enumerated value. Operating state
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to startup phase of inverter controller.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to execution of grid interface "auto-test" required by Italian country standard.
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to grid connection phase.
[7 empty] | 4 | MPPT |  |  | This state corresponds to inverter connected to grid and running with MPPT.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to inverter connected to grid and running with limited active power (derating).
[7 empty] | 6 | Shutting down (SHUTTING_DOWN) |  |  | This state corresponds to forced disconnection from grid (e.g. commanded by user through "remote off" command).
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to fault causing disconnection from grid.
[7 empty] | 8 | Standby (STANDBY) |  |  | This state corresponds to disconnection from grid caused by missing DC source or AC grid.
40109 | StVnd | Vendor Operating State |  | enum16 |  |  | supported |  | R | Vendor specific operating state code
40110 | Evt1 | Event1 |  | bitfield32 |  |  | supported |  | R | Bitmask value. Event fields
[7 empty] | Bit 0 | 1 = Ground fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = DC over voltage (DC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | AC disconnect open (AC_DISCONNECT)
[7 empty] | unimplemented | DC disconnect open (DC_DISCONNECT)
[7 empty] | Bit 4 | 1 = Grid shutdown (GRID_DISCONNECT) |  |  | This state corresponds to grid absence.
[7 empty] | unimplemented | Cabinet open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | Bit 8 | 1 = Frequency above limit (OVER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E006: Grid OF
[7 empty] | Bit 9 | 1 = Frequency under limit (UNDER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E007: Grid UF
[7 empty] | Bit 10 | 1 = AC Voltage above limit (AC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E003: Grid OV
[7 empty] | Bit 11 | 1 = AC Voltage under limit (AC_UNDER_VOLT) |  |  | This state corresponds to the following internal alarms: - E004: Grid UV
[7 empty] | unimplemented | Blown String fuse on input (BLOWN_STRING_FUSE)
[7 empty] | Bit 13 | 1 = Under temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Generic Memory or Communication error (internal) (MEMORY_LOSS) |  |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Hardware test failure (HW_TEST_FAILURE) |  |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
40112 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Reserved for future use
40114 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of active power derating: - Bit0: Power curtailment from external command - Bit1: Power limitation from Frequency-Watt - Bit2: Power limitation from high average grid voltage - Bit3: Power limitation from anti-islanding protection - Bit4: Power limitation from grid current rating limitation - Bit5: Power limitation for high temperature - Bit6: Power limitation for high DC voltage - Bit7: Reserved - Bit8: Power limitation from ramp-rate (connection ramp) - Bit9: Power limitation from momentary cessation - Bit10: Power limitation from ramp-rate (normal ramp-up) - Bit11: Power limitation from Volt-Watt - Bit12-31: Reserved
40116 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of apparent power derating: - Bit0: Power limitation for high temperature - Bit1: Power limitation for high DC voltage - Bit2-31: Reserved
40118 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of auxiliary devices: - Bit0: Fan fault - Bit1: Statistics memory fault - Bit2: RTC clock not set - Bit3: Reserved - Bit4: RTC low battery fault - Bit5: RTC quartz fault - Bit6-31: Reserved
40120 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | Fixed to 0 (reserved for future use)

## 120
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40122 | ID | Nameplate |  | uint16 |  |  | 120 |  |  | Inverter Controls Nameplate Ratings
40123 | L |  |  | uint16 |  |  | 26 |  |  | Model Length
40124 | DERTyp | DERTyp |  | enum16 |  |  | supported |  | R | Type of DER device. Default value is 4 to indicate PV device.
[7 empty] | 4 | PV
[7 empty] | 82 | PV_STOR
40125 | WRtg | WRtg |  | uint16 | W | WRtg_SF | supported |  | R | Continuous power output capability of the inverter.
40126 | WRtg_SF | WRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40127 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | supported |  | R | Continuous Volt-Ampere capability of the inverter.
40128 | VARtg_SF | VARtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40129 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 1.
40130 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 2.
40131 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 3.
40132 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 4.
40133 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40134 | ARtg | ARtg |  | uint16 | A | ARtg_SF | supported |  | R | Maximum RMS AC current level capability of the inverter. | Used as reference rating for current ramp-rate on M145.
40135 | ARtg_SF | ARtg_SF |  | sunssf |  |  | 0 |  | R | Scale factor
40136 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 1. | The PFRtgQ1 sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40137 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 2.
40138 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 3.
40139 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 4. | The PFRtgQ4 sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40140 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | -3 |  | R | Scale factor
40141 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | unimplemented |  | R | Nominal energy rating of storage device.
40142 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40143 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | unimplemented |  | R | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
40144 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for amp-hour rating.
40145 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer into the storage device.
40146 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40147 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer out of the storage device.
40148 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40149 | Pad | Pad |  | pad |  |  |  |  | R | Pad register.

## 121
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40150 | ID | Basic Settings |  | uint16 |  |  | 121 |  |  | Inverter Controls Basic Settings
40151 | L |  |  | uint16 |  |  | 30 |  |  | Model Length
40152 | WMax | WMax |  | uint16 | W | WMax_SF | supported |  | RW | Setting for maximum power output. Default to WRtg. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40153 | VRef | VRef |  | uint16 | V | VRef_SF | unimplemented |  | RW | Voltage at the PCC.
40154 | VRefOfs | VRefOfs |  | int16 | V | VRefOfs_SF | unimplemented |  | RW | Offset from PCC to inverter.
40155 | VMax | VMax |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for maximum voltage.
40156 | VMin | VMin |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for minimum voltage.
40157 | VAMax | VAMax |  | uint16 | VA | VAMax_SF | supported |  | RW | Setpoint for maximum apparent power. Default to VARtg. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40158 | VArMaxQ1 | VArMaxQ1 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit. Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40159 | VArMaxQ2 | VArMaxQ2 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
40160 | VArMaxQ3 | VArMaxQ3 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
40161 | VArMaxQ4 | VArMaxQ4 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
40162 | WGra | WGra |  | uint16 | % WMax/min | WGra_SF | supported |  | RW | Default ramp rate of change of active power due to command or internal action. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40163 | PFMinQ1 | PFMinQ1 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
40164 | PFMinQ2 | PFMinQ2 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
40165 | PFMinQ3 | PFMinQ3 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
40166 | PFMinQ4 | PFMinQ4 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
40167 | VArAct | VArAct |  | enum16 |  |  | unimplemented |  | RW | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
40168 | ClcTotVA | ClcTotVA |  | enum16 |  |  | unimplemented |  | RW | Calculation method for total apparent power. 1=vector 2=arithmetic.
40169 | MaxRmpRte | MaxRmpRte |  | uint16 | % WGra | MaxRmpRte_SF | unimplemented |  | RW | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
40170 | ECPNomHz | ECPNomHz |  | uint16 | Hz | ECPNomHz_SF | unimplemented |  | RW | Setpoint for nominal frequency at the ECP.
40171 | ConnPh | ConnPh |  | enum16 |  |  | unimplemented |  | RW | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
40172 | WMax_SF | WMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for real power.
40173 | VRef_SF | VRef_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for voltage at the PCC.
40174 | VRefOfs_SF | VRefOfs_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for offset voltage.
40175 | VMinMax_SF | VMinMax_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for min/max voltages.
40176 | VAMax_SF | VAMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for apparent power.
40177 | VArMax_SF | VArMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for reactive power.
40178 | WGra_SF | WGra_SF |  | sunssf |  |  | -1 |  | R | Scale factor for default ramp rate.
40179 | PFMin_SF | PFMin_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for minimum power factor.
40180 | MaxRmpRte_SF | MaxRmpRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for maximum ramp percentage.
40181 | ECPNomHz_SF | ECPNomHz_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for nominal frequency.

## 122
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40182 | ID | Measurements_Status |  | uint16 |  |  | 122 |  |  | Inverter Controls Extended Measurements and Status
40183 | L |  |  | uint16 |  |  | 44 |  |  | Model Length
40184 | PVConn | PVConn |  | bitfield16 |  |  | supported |  | R | PV inverter present/available status. Enumerated value.
[7 empty] | Bit 0 | 1 = CONNECTED
[7 empty] | unimplemented | AVAILABLE
[7 empty] | unimplemented | OPERATING
[7 empty] | unimplemented | TEST
40185 | StorConn | StorConn |  | bitfield16 |  |  | supported |  | R | Storage inverter present/available status. Enumerated value.
[7 empty] | Bit 0 | CONNECTED
[7 empty] | Bit 1 | AVAILABLE
[7 empty] | Bit 2 | OPERATING
[7 empty] | Bit 3 | TEST
40186 | ECPConn | ECPConn |  | bitfield16 |  |  | supported |  | R | ECP connection status: disconnected=0 connected=1.
[7 empty] | Bit 0 | 1 = CONNECTED
40187 | ActWh | ActWh |  | acc64 | Wh |  | supported |  | R | AC lifetime active (real) energy output. | Total exported active energy
40191 | ActVAh | ActVAh |  | acc64 | VAh |  | unimplemented |  | R | AC lifetime apparent energy output. | Total exported apparent energy
40195 | ActVArhQ1 | ActVArhQ1 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 1.
40199 | ActVArhQ2 | ActVArhQ2 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 2.
40203 | ActVArhQ3 | ActVArhQ3 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime negative energy output in quadrant 3.
40207 | ActVArhQ4 | ActVArhQ4 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 4.
40211 | VArAval | VArAval |  | int16 | var | VArAval_SF | unimplemented |  | R | Amount of VARs available without impacting watts output.
40212 | VArAval_SF | VArAval_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for available VARs.
40213 | WAval | WAval |  | uint16 | var | WAval_SF | unimplemented |  | R | Amount of Watts available.
40214 | WAval_SF | WAval_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for available Watts.
40215 | StSetLimMsk | StSetLimMsk |  | bitfield32 |  |  | supported |  | R | Bit Mask indicating setpoint limit(s) reached.
[7 empty] | Bit 0 | 1 = WMax
[7 empty] | Bit 1 | 1 = VAMax
[7 empty] | unimplemented | VArAval
[7 empty] | Bit 3 | 1 = VArMaxQ1 |  |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
[7 empty] | Bit 4 | 1 = VArMaxQ2
[7 empty] | Bit 5 | 1 = VArMaxQ3
[7 empty] | Bit 6 | 1 = VArMaxQ4
[7 empty] | unimplemented | PFMinQ1
[7 empty] | unimplemented | PFMinQ2
[7 empty] | unimplemented | PFMinQ3
[7 empty] | unimplemented | PFMinQ4
40217 | StActCtl | StActCtl |  | bitfield32 | 0 | 0 | supported |  | R | Bit Mask indicating which inverter controls are currently active.
[7 empty] | Bit 0 | 1 = FixedW
[7 empty] | Bit 1 | 1 = FixedVAR
[7 empty] | Bit 2 | 1 = FixedPF
[7 empty] | unimplemented | Volt-VAr
[7 empty] | unimplemented | Freq-Watt-Param
[7 empty] | unimplemented | Freq-Watt-Curve
[7 empty] | unimplemented | Dyn-Reactive-Current
[7 empty] | unimplemented | LVRT
[7 empty] | unimplemented | HVRT
[7 empty] | unimplemented | Watt-PF
[7 empty] | unimplemented | Volt-Watt
[7 empty] | unimplemented | Scheduled
[7 empty] | unimplemented | LFRT
[7 empty] | unimplemented | HFRT
40219 | TmSrc | TmSrc |  | string |  | unimplemented | unimplemented |  | R | Source of time synchronization.
40223 | Tms | Tms |  | uint32 | Secs |  | supported |  | R | Seconds since 01-01-2000 00:00 UTC
40225 | RtSt | RtSt |  | bitfield16 |  |  | supported |  | R | Bit Mask indicating active ride-through status.
[7 empty] | Bit 0 | 1 = LVRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 1 | 1 = HVRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 2 | 1 = LFRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 3 | 1 = HFRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
40226 | Ris | Ris |  | uint16 | ohms | Ris_SF | supported |  | R | Isolation resistance.
40227 | Ris_SF | Ris_SF |  | sunssf |  |  | 3 |  | R | Scale factor for isolation resistance.

## 123
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40228 | ID | Immediate Controls |  | uint16 |  |  | 123 |  |  | Immediate Inverter Controls | i. MaxLimPct: represents the target set-point of the active power control. - The set-point is expressed as % of WMax [group 121]; - The set point is calculated as WMaxLimPct *10^( WMaxLimPct_SF); - The target ouput power of the inverter is then calculated as WMax*10^(WMax_SF)*[WMaxLimPct *10^( WMaxLimPct_SF)]/100. ii. WMaxLimPct_WinTms: the time window is a period of time within which the inverter randomly delays before beginning execution of the command. iii. WMaxLimPct_RvrtTms: the reversion timeout value (if not zero) specifies a time for the requested change to revert to its default state. A timeout value of zero means the change persists until another change is made. If a reversion timer expires the control reverts to its default state. A timeout value of zero shall be avoided for closed loop control purpose. iv. WMaxLimPct_RmpTms: the ramp time is a fixed time in seconds, over which the inverter settings are to transition from their pre—setting level to their post—settings level v. WMaxLim_Ena represents the enable for the active power management according to the previously described 4 registers. WMaxLim_Ena is set at 0 by default and must be written to 1 to enable the active power reduction according to previous registers; In dynamic control funcitioning, the set-point is expected to be updated before the revision time WMaxLimPct_RvrtTms expires. To make effective the new active power settings it is needed to overwrite 1 to the enable WMaxLim_Ena register. Similar considerations apply to reactive power and power factor controls.
40229 | L |  |  | uint16 |  |  | 24 |  |  | Model Length
40230 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for connect/disconnect.
40231 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for connect/disconnect.
40232 | Conn | Conn |  | enum16 |  |  | supported |  | RW | Enumerated valued. Connection control.
[7 empty] | 0 | DISCONNECT
[7 empty] | 1 | CONNECT
40233 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | supported |  | RW | Set power output to specified level.
40234 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power limit change.
40235 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40236 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40237 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Throttle enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40238 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | supported |  | RW | Set power factor to specific value - cosine of angle.
40239 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power factor change.
40240 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power factor. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40241 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40242 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Fixed power factor enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40243 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | supported |  | RW | Reactive power in percent of WMax.
40244 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | supported |  | RW | Reactive power in percent of VArMax.
40245 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | unimplemented |  | RW | Reactive power in percent of VArAval.
40246 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for VAR limit change.
40247 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for VAR limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40248 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40249 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | supported |  | RW | Enumerated value. VAR percent limit mode. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | unimplemented | NONE
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40250 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Percent limit VAr enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40251 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for power output percent.
40252 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | -4 |  | R | Scale factor for power factor.
40253 | VArPct_SF | VArPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for reactive power percent.

## 126
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40254 | ID | Static Volt-VAR |  | uint16 |  |  | 126 |  |  | Static Volt-VAR Arrays | Monotony of curve: X values (Vn) for Volt-VAR curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-VArx) at once
40255 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40256 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40257 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-VAR control active.
[7 empty] | Bit 0 | 1 = ENABLED
40258 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-VAR change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40259 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-VAR curve selection.
40260 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40261 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40262 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximum of 20).
40263 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40264 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | scale factor for dependent variable.
40265 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40266 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40267 | DeptRef | DeptRef | 1 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40268 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40269 | VAr1 | VAr1 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40270 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40271 | VAr2 | VAr2 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40272 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40273 | VAr3 | VAr3 | 1 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40274 | V4 | V4 | 1 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40275 | VAr4 | VAr4 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40276 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40277 | VAr5 | VAr5 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40278 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40279 | VAr6 | VAr6 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40280 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40281 | VAr7 | VAr7 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40282 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40283 | VAr8 | VAr8 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40284 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40285 | VAr9 | VAr9 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40286 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40287 | VAr10 | VAr10 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40288 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40289 | VAr11 | VAr11 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40290 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40291 | VAr12 | VAr12 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40292 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40293 | VAr13 | VAr13 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40294 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40295 | VAr14 | VAr14 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40296 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40297 | VAr15 | VAr15 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40298 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40299 | VAr16 | VAr16 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40300 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40301 | VAr17 | VAr17 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40302 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40303 | VAr18 | VAr18 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40304 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40305 | VAr19 | VAr19 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40306 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40307 | VAr20 | VAr20 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40308 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40316 | RmpTms |  | 1 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40317 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40318 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40319 | ReadOnly | ReadOnly | 1 | enum16 |  | supported | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40320 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40321 | DeptRef | DeptRef | 2 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40322 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40323 | VAr1 | VAr1 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40324 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40325 | VAr2 | VAr2 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40326 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40327 | VAr3 | VAr3 | 2 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40328 | V4 | V4 | 2 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40329 | VAr4 | VAr4 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40330 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40331 | VAr5 | VAr5 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40332 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40333 | VAr6 | VAr6 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40334 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40335 | VAr7 | VAr7 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40336 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40337 | VAr8 | VAr8 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40338 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40339 | VAr9 | VAr9 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40340 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40341 | VAr10 | VAr10 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40342 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40343 | VAr11 | VAr11 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40344 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40345 | VAr12 | VAr12 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40346 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40347 | VAr13 | VAr13 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40348 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40349 | VAr14 | VAr14 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40350 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40351 | VAr15 | VAr15 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40352 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40353 | VAr16 | VAr16 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40354 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40355 | VAr17 | VAr17 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40356 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40357 | VAr18 | VAr18 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40358 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40359 | VAr19 | VAr19 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40360 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40361 | VAr20 | VAr20 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40362 | CrvNam | CrvNam | 2 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40370 | RmpTms |  | 2 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40371 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40372 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40373 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
40374 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40375 | DeptRef | DeptRef | 3 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40376 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40377 | VAr1 | VAr1 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40378 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40379 | VAr2 | VAr2 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40380 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40381 | VAr3 | VAr3 | 3 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40382 | V4 | V4 | 3 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40383 | VAr4 | VAr4 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40384 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40385 | VAr5 | VAr5 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40386 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40387 | VAr6 | VAr6 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40388 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40389 | VAr7 | VAr7 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40390 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40391 | VAr8 | VAr8 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40392 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40393 | VAr9 | VAr9 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40394 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40395 | VAr10 | VAr10 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40396 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40397 | VAr11 | VAr11 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40398 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40399 | VAr12 | VAr12 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40400 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40401 | VAr13 | VAr13 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40402 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40403 | VAr14 | VAr14 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40404 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40405 | VAr15 | VAr15 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40406 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40407 | VAr16 | VAr16 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40408 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40409 | VAr17 | VAr17 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40410 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40411 | VAr18 | VAr18 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40412 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40413 | VAr19 | VAr19 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40414 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40415 | VAr20 | VAr20 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40416 | CrvNam | CrvNam | 3 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40424 | RmpTms |  | 3 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40425 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40426 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40427 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
40428 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40429 | DeptRef | DeptRef | 4 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40430 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40431 | VAr1 | VAr1 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40432 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40433 | VAr2 | VAr2 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40434 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40435 | VAr3 | VAr3 | 4 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40436 | V4 | V4 | 4 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40437 | VAr4 | VAr4 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40438 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40439 | VAr5 | VAr5 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40440 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40441 | VAr6 | VAr6 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40442 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40443 | VAr7 | VAr7 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40444 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40445 | VAr8 | VAr8 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40446 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40447 | VAr9 | VAr9 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40448 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40449 | VAr10 | VAr10 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40450 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40451 | VAr11 | VAr11 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40452 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40453 | VAr12 | VAr12 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40454 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40455 | VAr13 | VAr13 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40456 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40457 | VAr14 | VAr14 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40458 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40459 | VAr15 | VAr15 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40460 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40461 | VAr16 | VAr16 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40462 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40463 | VAr17 | VAr17 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40464 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40465 | VAr18 | VAr18 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40466 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40467 | VAr19 | VAr19 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40468 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40469 | VAr20 | VAr20 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40470 | CrvNam | CrvNam | 4 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40478 | RmpTms |  | 4 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40479 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40480 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40481 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.

## 127
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40482 | ID | Freq-Watt Param |  | uint16 |  |  | 127 |  |  | Parameterized Frequency-Watt
40483 | L |  |  | uint16 |  |  | 10 |  |  | Model Length
40484 | WGra | WGra |  | uint16 | % PM/Hz | WGra_SF | supported |  | RW | The slope of the reduction in the maximum allowed watts output as a function of frequency. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40485 | HzStr | HzStr |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
40486 | HzStop | HzStop |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
40487 | HysEna | HysEna |  | bitfield16 |  |  | supported |  | RW | Enable hysterisis
[7 empty] | Bit 0 | 1 = ENABLED
40488 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Parameterized Frequency-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40489 | HzStopWGra | HzStopWGra |  | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
40490 | WGra_SF | WGra_SF |  | sunssf |  |  | 0 |  | R | Scale factor for output gradient.
40491 | HzStrStop_SF | HzStrStop_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency deviations.
40492 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40493 | Pad |  |  | pad |  |  |  |  | R

## 129
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40494 | ID | LVRTD |  | uint16 |  |  | 129 |  |  | LVRT Must Disconnect
40495 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40496 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40497 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40498 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LVRT change.
40499 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LVRT curve selection.
40500 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40501 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40502 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40503 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40504 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40505 | Pad |  |  | pad |  |  |  |  | R
40506 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40507 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40508 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40509 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40510 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40511 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40512 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40513 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40514 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40515 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40516 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40517 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40518 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40519 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40520 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40521 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40522 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40523 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40524 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40525 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40526 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40527 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40528 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40529 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40530 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40531 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40532 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40533 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40534 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40535 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40536 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40537 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40538 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40539 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40540 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40541 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40542 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40543 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40544 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40545 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40546 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40547 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40555 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 130
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40556 | ID | HVRTD |  | uint16 |  |  | 130 |  |  | HVRT Must Disconnect
40557 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40558 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40559 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40560 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HVRT change.
40561 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HVRT curve selection.
40562 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40563 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40564 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40565 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40566 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40567 | Pad |  |  | pad |  |  |  |  | R
40568 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40569 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40570 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40571 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40572 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40573 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40574 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40575 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40576 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40577 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40578 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40579 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40580 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40581 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40582 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40583 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40584 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40585 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40586 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40587 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40588 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40589 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40590 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40591 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40592 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40593 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40594 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40595 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40596 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40597 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40598 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40599 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40600 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40601 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40602 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40603 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40604 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40605 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40606 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40607 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40608 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40609 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40617 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 132
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40618 | ID | Volt-Watt |  | uint16 |  |  | 132 |  |  | Volt-Watt | Monotony of curve: X values (Vn) for Volt-Watt curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-Wx) at once
40619 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40620 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40621 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40622 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-watt change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40623 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-watt curve selection.
40624 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40625 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend min. 4).
40626 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of points in array (maximum 20).
40627 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40628 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | Scale Factor for % DeptRef
40629 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40630 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40631 | DeptRef | DeptRef | 1 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40632 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40633 | W1 | W1 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40634 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40635 | W2 | W2 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40636 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40637 | W3 | W3 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40638 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40639 | W4 | W4 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40640 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40641 | W5 | W5 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40642 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40643 | W6 | W6 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40644 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40645 | W7 | W7 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40646 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40647 | W8 | W8 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40648 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40649 | W9 | W9 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40650 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40651 | W10 | W10 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40652 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40653 | W11 | W11 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40654 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40655 | W12 | W12 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40656 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40657 | W13 | W13 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40658 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40659 | W14 | W14 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40660 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40661 | W15 | W15 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40662 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40663 | W16 | W16 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40664 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40665 | W17 | W17 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40666 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40667 | W18 | W18 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40668 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40669 | W19 | W19 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40670 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40671 | W20 | W20 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40672 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40680 | RmpPt1Tms | RmpPt1Tms | 1 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40681 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40682 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40683 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40684 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40685 | DeptRef | DeptRef | 2 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40686 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40687 | W1 | W1 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40688 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40689 | W2 | W2 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40690 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40691 | W3 | W3 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40692 | V4 | V4 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40693 | W4 | W4 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40694 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40695 | W5 | W5 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40696 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40697 | W6 | W6 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40698 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40699 | W7 | W7 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40700 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40701 | W8 | W8 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40702 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40703 | W9 | W9 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40704 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40705 | W10 | W10 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40706 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40707 | W11 | W11 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40708 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40709 | W12 | W12 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40710 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40711 | W13 | W13 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40712 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40713 | W14 | W14 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40714 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40715 | W15 | W15 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40716 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40717 | W16 | W16 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40718 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40719 | W17 | W17 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40720 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40721 | W18 | W18 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40722 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40723 | W19 | W19 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40724 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40725 | W20 | W20 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40726 | CrvNam | CrvNam | 2 | string |  |  | supported |  | RW | Optional description for curve.
40734 | RmpPt1Tms | RmpPt1Tms | 2 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40735 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40736 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40737 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40738 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40739 | DeptRef | DeptRef | 3 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40740 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40741 | W1 | W1 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40742 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40743 | W2 | W2 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40744 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40745 | W3 | W3 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40746 | V4 | V4 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40747 | W4 | W4 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40748 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40749 | W5 | W5 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40750 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40751 | W6 | W6 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40752 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40753 | W7 | W7 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40754 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40755 | W8 | W8 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40756 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40757 | W9 | W9 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40758 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40759 | W10 | W10 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40760 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40761 | W11 | W11 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40762 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40763 | W12 | W12 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40764 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40765 | W13 | W13 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40766 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40767 | W14 | W14 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40768 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40769 | W15 | W15 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40770 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40771 | W16 | W16 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40772 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40773 | W17 | W17 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40774 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40775 | W18 | W18 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40776 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40777 | W19 | W19 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40778 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40779 | W20 | W20 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40780 | CrvNam | CrvNam | 3 | string |  |  | supported |  | RW | Optional description for curve.
40788 | RmpPt1Tms | RmpPt1Tms | 3 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40789 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40790 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40791 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40792 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40793 | DeptRef | DeptRef | 4 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40794 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40795 | W1 | W1 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40796 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40797 | W2 | W2 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40798 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40799 | W3 | W3 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40800 | V4 | V4 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40801 | W4 | W4 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40802 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40803 | W5 | W5 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40804 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40805 | W6 | W6 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40806 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40807 | W7 | W7 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40808 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40809 | W8 | W8 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40810 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40811 | W9 | W9 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40812 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40813 | W10 | W10 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40814 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40815 | W11 | W11 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40816 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40817 | W12 | W12 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40818 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40819 | W13 | W13 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40820 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40821 | W14 | W14 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40822 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40823 | W15 | W15 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40824 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40825 | W16 | W16 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40826 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40827 | W17 | W17 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40828 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40829 | W18 | W18 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40830 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40831 | W19 | W19 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40832 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40833 | W20 | W20 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40834 | CrvNam | CrvNam | 4 | string |  |  | supported |  | RW | Optional description for curve.
40842 | RmpPt1Tms | RmpPt1Tms | 4 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40843 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40844 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40845 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.

## 135
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40846 | ID | LFRT |  | uint16 |  |  | 135 |  |  | Low Frequency Ride-through | Monotony of curve: X values (Vn) for Volt-Watt curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-Wx) at once
40847 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40848 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40849 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LHzRT control mode. Enable active curve. Bitfield value.
[7 empty] | Bit 0 | 1 = ENABLED
40850 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LFRT change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40851 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LFRT curve selection.
40852 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40853 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40854 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40855 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40856 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency.
40857 | Pad |  |  | pad |  |  |  |  | R
40858 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40859 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40860 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40861 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40862 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40863 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40864 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40865 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40866 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40867 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40868 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40869 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40870 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40871 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40872 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40873 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40874 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40875 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40876 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40877 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40878 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40879 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40880 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40881 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40882 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40883 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40884 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40885 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40886 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40887 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40888 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40889 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40890 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40891 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40892 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40893 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40894 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40895 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40896 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40897 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40898 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40899 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40907 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.

## 136
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40908 | ID | HFRT |  | uint16 |  |  | 136 |  |  | High Frequency Ride-through
40909 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40910 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40911 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HFRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40912 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HFRT change.
40913 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HFRT curve selection.
40914 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40915 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40916 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40917 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40918 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency.
40919 | Pad |  |  | pad |  |  |  |  | R
40920 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40921 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40922 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40923 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40924 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40925 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40926 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40927 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40928 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40929 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40930 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40931 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40932 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40933 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40934 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40935 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40936 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40937 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40938 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40939 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40940 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40941 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40942 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40943 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40944 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40945 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40946 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40947 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40948 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40949 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40950 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40951 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40952 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40953 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40954 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40955 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40956 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40957 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40958 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40959 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40960 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40961 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40969 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 139
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40970 | ID | LVRTX |  | uint16 |  |  | 139 |  |  | LVRT extended curve
40971 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40972 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40973 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED |  |  | The enable of LVRT is shared with HVRT so setting this bit has the same effect on "ModEna" register of M140.
40974 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | RW | Time window for LVRT change.
40975 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for LVRT curve selection.
40976 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40977 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40978 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40979 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40980 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40981 | CrvType |  |  | enum16 |  |  | supported |  | R
[7 empty] | 1 | CEASE_TO_ENERGIZE
40982 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40983 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 1 duration.
40984 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40985 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 2 duration.
40986 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 2 voltage.
40987 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 3 duration.
40988 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 3 voltage.
40989 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 4 duration.
40990 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 4 voltage.
40991 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 5 duration.
40992 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 5 voltage.
40993 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 6 duration.
40994 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 6 voltage.
40995 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 duration.
40996 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 voltage.
40997 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 duration.
40998 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 voltage.
40999 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 duration.
41000 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 voltage.
41001 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 duration.
41002 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 voltage.
41003 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 duration.
41004 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 voltage.
41005 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 duration.
41006 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 voltage.
41007 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 duration.
41008 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 voltage.
41009 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 duration.
41010 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 voltage.
41011 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 duration.
41012 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 voltage.
41013 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 duration.
41014 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 voltage.
41015 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 duration.
41016 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 voltage.
41017 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 duration.
41018 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 voltage.
41019 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 duration.
41020 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 voltage.
41021 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 duration.
41022 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 voltage.
41023 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
41031 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 140
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | Value | R/W | Description from RefModel | Conformance Notes
41032 | ID | HVRTX |  | uint16 |  |  | 140 |  | 140 |  | HVRT extended curve
41033 | L |  |  | uint16 |  |  | 60 |  | 60 |  | Model Length
41034 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | supported | RW | Index of active curve. 0=no active curve.
41035 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | supported | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED | supported |  |  | The enable of HVRT is shared with LVRT so setting this bit has the same effect on "ModEna" register of M139.
41036 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | unimplemented | RW | Time window for LVRT change.
41037 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | unimplemented | RW | Timeout period for LVRT curve selection.
41038 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | unimplemented | RW | Ramp time for moving from current mode to new mode.
41039 | NCrv | NCrv |  | uint16 |  |  | supported |  | supported | R | Number of curves supported (recommend 4).
41040 | NPt | NPt |  | uint16 |  |  | supported |  | supported | R | Number of curve points supported (maximumn of 20).
41041 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | -2 | R | Scale factor for duration.
41042 | V_SF | V_SF |  | sunssf |  |  | -1 |  | -1 | R | Scale factor for percent VRef.
41043 | CrvType |  |  | enum16 |  |  | supported |  | supported | R
[7 empty] | 1 | CEASE_TO_ENERGIZE | supported
41044 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | supported | RW | Number of active points in array.
41045 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 1 duration.
41046 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | supported | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41047 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 2 duration.
41048 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 2 voltage.
41049 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 3 duration.
41050 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 3 voltage.
41051 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 4 duration.
41052 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 4 voltage.
41053 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 5 duration.
41054 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 5 voltage.
41055 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 6 duration.
41056 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 6 voltage.
41057 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 7 duration.
41058 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 7 voltage.
41059 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 8 duration.
41060 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 8 voltage.
41061 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 9 duration.
41062 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 9 voltage.
41063 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 10 duration.
41064 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 10 voltage.
41065 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 11 duration.
41066 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 11 voltage.
41067 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 12 duration.
41068 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 12 voltage.
41069 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 13 duration.
41070 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 13 voltage.
41071 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 14 duration.
41072 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 14 voltage.
41073 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 15 duration.
41074 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 15 voltage.
41075 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 16 duration.
41076 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 16 voltage.
41077 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 17 duration.
41078 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 17 voltage.
41079 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 18 duration.
41080 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 18 voltage.
41081 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 19 duration.
41082 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 19 voltage.
41083 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | unimplemented | RW | Point 20 duration.
41084 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | unimplemented | RW | Point 20 voltage.
41085 | CrvNam | CrvNam | 1 | string |  |  | supported |  | supported | RW | Optional description for curve.
41093 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | supported | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | supported | READWRITE | supported
[7 empty] | unimplemented | READONLY | supported

## 145
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41094 | ID | Extended Settings |  | uint16 |  |  | 145 |  |  | Inverter controls extended settings
41095 | L | [5 empty] | 8 |  |  | Model Length
41096 | NomRmpUpRte | Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41097 | NomRmpDnRte | NomRmpDnRte |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp down rate as a percentage of max current.
41098 | EmgRmpUpRte | Emergency Ramp Up Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41099 | EmgRmpDnRte | Emergency Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41100 | ConnRmpUpRte | Connect Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Connect ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41101 | ConnRmpDnRte | Connect Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Connect ramp down rate as a percentage of max current.
41102 | AGra | Default Ramp Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp rate specified in percent of max current.
41103 | Rmp_SF | Ramp Rate Scale Factor |  | sunssf |  |  | -1 |  | R | Ramp Rate Scale Factor

## 160
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41104 | ID | Multiple MPPT Inverter Extension Model |  | uint16 |  |  | 160 |  |  |  | Configuration of MPPT channels: Target product supports vendor-specific configuration of MPPT channels, also known as "input mode". The following configuration modes are supported: - Independent MPPT: A separate MPPT control runs on each channel so state conditions (e.g. "DCSt" register on M160 repeating blocks) are independent. - Parallel MPPT: Channel are connected in parallel to the same source and a unique MPPT control runs for all of them so many state conditions (e.g. "DCSt" register on M160 repeating blocks) are redundant.
41105 | L |  |  | uint16 |  |  | 48 |  |  | Model Length
41106 | DCA_SF | Current Scale Factor |  | sunssf |  |  | -1 |  | R
41107 | DCV_SF | Voltage Scale Factor |  | sunssf |  |  | -1 |  | R
41108 | DCW_SF | Power Scale Factor |  | sunssf |  |  | 1 |  | R
41109 | DCWH_SF | Energy Scale Factor |  | sunssf |  |  | unimplemented |  | R
41110 | Evt | Global Events |  | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 =Ground Fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 =Input Over Voltage (INPUT_OVER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 =Manual Shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 =Over Temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Memory Loss (MEMORY_LOSS) |  |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | Bit 20 | 1 = Test Failed (TEST_FAILED) |  |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  |  | This state corresponds to the following internal alarms: - E001: Input OC
41112 | N | Number of Modules |  | count |  |  | supported |  | R
41113 | TmsPer | Timestamp Period |  | uint16 |  |  | unimplemented |  | R
41114 | ID | Input ID | 1 | uint16 |  |  | supported |  | R
41115 | IDStr | Input ID Sting | 1 | string |  |  | supported |  | R
41123 | DCA | DC Current | 1 | uint16 | A | DCA_SF | supported |  | R
41124 | DCV | DC Voltage | 1 | uint16 | V | DCV_SF | supported |  | R
41125 | DCW | DC Power | 1 | uint16 | W | DCW_SF | supported |  | R
41126 | DCWH | Lifetime Energy | 1 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41128 | Tms | Timestamp | 1 | uint32 | Secs |  | unimplemented |  | R
41130 | Tmp | Temperature | 1 | int16 | C |  | unimplemented |  | R
41131 | DCSt | Operating State | 1 | enum16 |  |  | supported |  | R
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to unloaded/disconnected DC channel.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to connected DC channel but not ready for starting MPPT (e.g. for low voltage condition).
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to connected DC channel starting MPPT regulation.
[7 empty] | 4 | MPPT |  |  | This state corresponds to connected DC channel running MPPT regulation.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to connected DC channel with forced MPPT suspension (e,g, for by-pass or power-saving purposes).
[7 empty] | unimplemented | Shutting Down (SHUTTING_DOWN)
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to connected DC channel with pending fault (under-voltage, over-voltage, over-current).
[7 empty] | unimplemented | Standby (STANDBY)
[7 empty] | unimplemented | Test (TEST)
[7 empty] | unimplemented | Reserved (RESERVED)
41132 | DCEvt | Module Events | 1 | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 =Ground Fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 =Input Over Voltage (INPUT_OVER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 =Manual Shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 =Over Temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Memory Loss (MEMORY_LOSS) |  |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | Bit 20 | 1 = Test Failed (TEST_FAILED) |  |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  |  | This state corresponds to the following internal alarms: - E001: Input OC
41134 | ID | Input ID | 2 | uint16 |  |  | supported |  | R
41135 | IDStr | Input ID Sting | 2 | string |  |  | supported |  | R
41143 | DCA | DC Current | 2 | uint16 | A | DCA_SF | supported |  | R
41144 | DCV | DC Voltage | 2 | uint16 | V | DCV_SF | supported |  | R
41145 | DCW | DC Power | 2 | uint16 | W | DCW_SF | supported |  | R
41146 | DCWH | Lifetime Energy | 2 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41148 | Tms | Timestamp | 2 | uint32 | Secs |  | unimplemented |  | R
41150 | Tmp | Temperature | 2 | int16 | C |  | unimplemented |  | R
41151 | DCSt | Operating State | 2 | enum16 |  |  | supported |  | R
41152 | DCEvt | Module Events | 2 | bitfield32 |  |  | supported |  | R
| DCV | DC Voltage
| DCW | DC Power
| DCWH | Lifetime Energy
| Tms | Timestamp
| Tmp | Temperature
| DCSt | Operating State
| DCEvt | Module Events

## 65230
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41154 | ID | [5 empty] | 65230
41155 | L | [5 empty] | 1
41156 | LatchRest_Ena |  |  | enum16 |  |  | supported |  | RW | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. Write register to 1 (ENABLED) for removing a latch condition; immediately after, register is automatically set to 0.

## 65232
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41157 | ID | Additional Functions |  | uint16 |  |  | 65232 |  | R | Additional Functions vendor model
41158 | L |  |  | uint16 |  |  | 20 |  | R | Model Length
41159 | GNDKit _Inst | Gounding kit |  | enum16 |  |  | unimplemented |  | R | Presence of Grounding kit. The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41160 | RSDBleed_Inst | Rapid Shut Down Compatibility Kit |  | enum16 |  |  | unimplemented |  | R | Presence of Rapid Shut Down Compatibility Kit.
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41161 | QNT_Inst | Pre-Charge Kit |  | enum16 |  |  | unimplemented |  | R | Presence of PreCharge kit The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41162 | PID _Inst | Anti-PID Kit |  | enum16 |  |  | unimplemented |  | R | Presence of Anti-PID kit The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41163 | Vneg_GND | Vneg-gnd |  | uint16 | V | VGND_SF | unimplemented |  | R | Measured Voltage between DC Negative Pole and Ground
41164 | Vpos_GND | Vpos-gnd |  | uint16 | V | VGND_SF | unimplemented |  | R | Measured Voltage between DC Positive Pole and Ground
41165 | Night_Mod_State | Night Reactive Power Status |  | enum16 |  |  | unimplemented |  | R | Current Time status for Reactive Power Mode, during night time the Night Reactive Power Mode is applied
[7 empty] | 0 | DAY TIME
[7 empty] | 1 | NIGHT TIME
41166 | DS_Ena | Energy Save Mode |  | enum16 |  |  | unimplemented |  | RW | Energy Save mode enabler. When the inverter is in Energy Save mode the night consumption will be reduced and measures will not be available during night time
41167 | Night_Mod | Night Reactive Power Mode |  | enum16 |  |  | unimplemented |  | RW | Settings for Night Reactive Power Mode. In case of Reactive Power is suggested to use the reactive power set point on model 123 for Plant Control purpose. Night TIme Reactive Power is mutually exclusive with Anti-PID mode, when Anti-PID mode is enabled the Night Reactive Power will be automatically disabled and vice-versa
[7 empty] | 0 | DISABLED
[7 empty] | 1 | REACTIVE POWER
[7 empty] | 2 | VOLT-VAR REACTIVE_POWER
41168 | QFixVArMaxPct | Night Q Fix Set-Point |  | int16 | % VAMax or % WMax or % VArMax | NightQFix_SF | unimplemented |  | RW | Fixed Reactive Power compensation during Night Time, for dynamic behavior with a Plant Control it is mandatory to use the reactive power set point on data model 123. The set Point can be espressed as % of % VAMax, % WMax or % VArMax according to the reactive power mode VArPct_Mod available data model 123 - Immediate Control
41169 | Anti_PID_State | Anti-PID Status |  | enum16 |  |  | unimplemented |  | R | Anti-PID mode running info, the Anti-PID function will be running when activated during night time
[7 empty] | 0 | NOT RUNNING
41178 | [6 empty] | 1 | RUNNING
41170 | Anti_PID_Mod | Anti-PID Mode |  | enum16 |  |  | unimplemented |  | RW | Anti-PID mode enabler. Anti-PID is mutually exclusive with Night Reactive Power mode, when Anti-PID mode is enabled the Night Reactive Power will be automatically disabled and vice-versa
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
41171 | PID_VRef | Anti-PID Reference Voltage |  | enum16 |  |  | unimplemented |  | RW | Inverter will apply an Anti-PID Reference Voltage to the PV panels when the Anti-PID function is running. NOTE: Anti-PID Lock out voltage + Anti-PID Reference Voltage MUST be below 1500VDc and the inverter will not allow any change that are not compatible with this constraint
[7 empty] | 0 | 500V
[7 empty] | 1 | 650V
[7 empty] | 2 | 800V
41172 | PID_Thr | Anti-PID Lock-In/Out Voltage |  | enum16 |  |  | unimplemented |  | RW | Lock In Voltage (first value) defines when the Anti-PID function will be activacted. At night, when the DC voltage drop down continuouly below the Anti-PID Lock In Voltage for a time greater than PID_Delay the inverter activates the Anti-PID function and will provide the reference voltage to the PV Panels. Lock Out Voltage (second value) is always equal to the Lock In Voltage + 10%Min Vstart and defines when the Anti-PID function will be deactivacted. At morning, when the DC Voltage increase above the Anti-PID Lock Out Voltage the inverter deactivates the Anti-PID function and will start to convert the DC power into the grid. MinVstart is the minimum Starting Voltage between all the MPPTs. NOTE: Anti-PID Lock out voltage + Anti-PID Reference Voltage MUST be below 1500VDc and the inverter will not allow any change that are not compatible with this constraint
[7 empty] | 0 | 10%MinVstart / 20%MinVstart
[7 empty] | 1 | 20%MinVstart / 30%MinVstart
[7 empty] | 2 | 30%MinVstart / 40%MinVstart
[7 empty] | 3 | 40%MinVstart / 50% MinVstart
41173 | PID_Delay | Anti-PID Starting Delay |  | uint16 | min |  | unimplemented |  | RW | Time windows used to assure that the voltage is steadily below the Anti-PID Lock In Voltage. Inverter activate the Anti-PID function only when the DC voltage drop down continuouly below the Anti-PID Lock In Voltage for a time greater than PID_Delay
41174 | VGND_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Pole to Ground measures
41175 | NightQFix_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale factor for Fixed Reactive Power Set Point
41176 | Reserved | [8 empty] | Reserved for future scope
41177 | Reserved | [8 empty] | Reserved for future scope
41178 | Reserved | [8 empty] | Reserved for future scope

## 65233
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41179 | ID | Multiple Meter |  | uint16 |  |  | 65233 |  |  | Multiple Meter vendor model
41180 | L |  |  | uint16 |  |  | 183 |  |  | Model Length
41181 | RatioTrns_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Transformers Ratio
41182 | V_SF |  |  | sunssf |  |  | -1 |  | R | Scale Factor for Voltage
41183 | A_SF |  |  | sunssf |  |  | -1 |  | R | Scale Factor for Current
41184 | W_SF |  |  | sunssf |  |  | 1 |  | R | Scale Factor for Active Power
41185 | VAr_SF |  |  | sunssf |  |  | 1 |  | R | Scale Factor for Reactive Power
41186 | VA_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Apparent Power
41187 | PF_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Power Factor
41188 | Hz_SF |  |  | sunssf |  |  | -2 |  | R | Scale Factor for Frequency
41189 | WH_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Active Energy
41190 | VArH_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Reactive Energy
41191 | Thd_SF |  |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Total Harmonic Distorsion
41192 | N | Number of modules |  | uint16 |  |  | supported |  | R | Number of meter
41193 | Pos | Meter insertion position | 1 | enum16 |  |  | unimplemented |  | R | Position of meter
[7 empty] | 0 | POC |  | Meter mounted on point of common connection
[7 empty] | 1 | INV |  | Meter mounted on inverter
[7 empty] | 2 | LOAD |  | Meter on load
41194 | InsMd | Meter grid insertion mode | 1 | enum16 |  |  | supported |  | R | Meter connected phases
[7 empty] | 0 | L123 |  | Meter inserted on all phases
[7 empty] | 1 | L1 |  | Meter inserted on individual phase L1
[7 empty] | 2 | L2 |  | Meter inserted on individual phase L2
[7 empty] | 3 | L3 |  | Meter inserted on individual phase L3
41195 | Mn | Manufacturer | 1 | string |  |  | supported |  | R | Manufacturer specific value
41211 | Md | Model | 1 | string |  |  | supported |  | R | Manufacturer specific value
41227 | Opt | Options | 1 | string |  |  | unimplemented |  | R | Manufacturer specific value
41235 | Vr | Version | 1 | string |  |  | supported |  | R | Manufacturer specific value
41243 | SN | Serial Number | 1 | string |  |  | supported |  | R | Manufacturer specific value
41259 | DA | Device Address | 1 | uint16 |  |  | supported |  | R | Modbus device address
41260 | IP_ADD | IP Address | 1 | ip32 |  |  | unimplemented |  | R | Device IP address
41262 | Sign | Energy measure sign | 1 | enum16 |  |  | unimplemented |  | R | CT Reverse option enabled
[7 empty] | 0 | NON_INVERTED |  | Energy measurement sign not reversed
[7 empty] | 1 | INVERTED |  | Energy measurement sign reversed
41263 | RatioTrnsA | Current transformer ratio | 1 | uint16 | Pct | RatioTrns_SF | unimplemented |  | R | Current transformer ratio
41264 | RatioTrnsV | Voltage transformer ratio | 1 | uint16 | Pct | RatioTrns_SF | unimplemented |  | R | Voltage transformer ratio
41265 | PPVph12 | Phase Voltage L1-L2 | 1 | uint16 | V | V_SF | unimplemented |  | R | Phase to Phase Voltage L1-L2
41266 | PPVph23 | Phase Voltage L2-L3 | 1 | uint16 | V | V_SF | unimplemented |  | R | Phase to Phase Voltage L1-L3
41267 | PPVph31 | Phase Voltage L3-L1 | 1 | uint16 | V | V_SF | unimplemented |  | R | Phase to Phase Voltage L3-L1
41268 | PhVph1 | Phase Voltage L1-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L1
41269 | PhVph2 | Phase Voltage L2-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L2
41270 | PhVph3 | Phase Voltage L3-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L3
41271 | Aph1 | Amps Phase L1 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L1
41272 | Aph2 | Amps Phase L2 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L2
41273 | Aph3 | Amps Phase L3 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L3
41274 | A | Amps | 1 | uint16 | A | A_SF | unimplemented |  | R | Total Current
41275 | Wph1 | Watts L1 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L1
41276 | Wph2 | Watts L2 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L2
41277 | Wph3 | Watts L3 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L3
41278 | W | Watts | 1 | int16 | W | W_SF | supported |  | R | Total Active Power
41279 | VArPh1 | Reactive Power L1 | 1 | int16 | W | VAr_SF | supported |  | R | Total Reactive Power on Phase L1
41280 | VArPh2 | Reactive Power L2 | 1 | int16 | W | VAr_SF | supported |  | R | Total Reactive Power on Phase L2
41281 | VArPh3 | Reactive Power L3 | 1 | int16 | W | VAr_SF | supported |  | R | Total Reactive Power on Phase L3
41282 | VAr | Reactive Power | 1 | int16 | W | VAr_SF | supported |  | R | Total Reactive Power
41283 | VAph1 | Apparent Power L1 | 1 | int16 | W | VA_SF | unimplemented |  | R | Total Apparent Power on Phase L1
41284 | VAph2 | Apparent Power L2 | 1 | int16 | W | VA_SF | unimplemented |  | R | Total Apparent Power on Phase L2
41285 | VAph3 | Apparent Power L3 | 1 | int16 | W | VA_SF | unimplemented |  | R | Total Apparent Power on Phase L3
41286 | VA | Apparent Power | 1 | int16 | W | VA_SF | unimplemented |  | R | Total Apparent Power
41287 | PF1 | PF L1 | 1 | int16 | Pct | PF_SF | unimplemented |  | R | Power Factor on Phase L1
41288 | PF2 | PF L2 | 1 | int16 | Pct | PF_SF | unimplemented |  | R | Power Factor on Phase L2
41289 | PF3 | PF L3 | 1 | int16 | Pct | PF_SF | unimplemented |  | R | Power Factor on Phase L3
41290 | PF | PF | 1 | int16 | Pct | PF_SF | unimplemented |  | R | Overall Power Factor
41291 | Hz | Grid frequency | 1 | uint16 | Hz | Hz_SF | supported |  | R | Grid frequency
41292 | WHimp | Active Imported Energy | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Total Active Imported Energy
41296 | WHexp | Active Exported Energy | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Total Active Exported Energy
41300 | WHimp1 | Active Imported Energy L1 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Imported Energy on Phase L1
41304 | WHimp2 | Active Imported Energy L2 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Imported Energy on Phase L2
41308 | WHimp3 | Active Imported Energy L3 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Imported Energy on Phase L3
41312 | WHexp1 | Active Exported Energy L1 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Exported Energy on Phase L1
41316 | WHexp2 | Active Exported Energy L2 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Exported Energy on Phase L2
41320 | WHexp3 | Active Exported Energy L3 | 1 | acc64 | Wh | WH_SF | unimplemented |  | R | Active Exported Energy on Phase L3
41324 | VArHimp | Reactive Imported Energy | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Total Reactive Imported Energy
41328 | VArHexp | Reactive Exported Energy | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Total Reactive Exported Energy
41332 | VArHimp1 | Reactive Imported Energy L1 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Imported Energy on Phase L1
41336 | VArHexp1 | Reactive Exported Energy L1 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Imported Energy on Phase L2
41340 | VArHimp2 | Reactive Imported Energy L2 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Imported Energy on Phase L3
41344 | VArHexp2 | Reactive Exported Energy L2 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Exported Energy on Phase L1
41348 | VArHimp3 | Reactive Imported Energy L3 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Exported Energy on Phase L2
41352 | VArHexp3 | Reactive Exported Energy L3 | 1 | acc64 | Wh | VArH_SF | unimplemented |  | R | Reactive Exported Energy on Phase L3
41356 | ThdV1 | Total voltage harmonic distortion % L1 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total voltage harmonic distortion % on Phase L1
41357 | ThdV2 | Total voltage harmonic distortion % L2 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total voltage harmonic distortion % on Phase L2
41358 | ThdV3 | Total voltage harmonic distortion % L3 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total voltage harmonic distortion % on Phase L3
41359 | ThdV | Total voltage harmonic distortion % | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Overall voltage harmonic distortion %
41360 | ThdA1 | Total current harmonic distortion % L1 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total current harmonic distortion % on Phase L1
41361 | ThdA2 | Total current harmonic distortion % L2 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total current harmonic distortion % on Phase L2
41362 | ThdA3 | Total current harmonic distortion % L3 | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Total current harmonic distortion % on Phase L3
41363 | ThdA | Total current harmonic distortion % | 1 | uint16 | Pct | Thd_SF | unimplemented |  | R | Overall current harmonic distortion %

## 65234
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41364 | ID | Battery Data |  |  |  |  | 65234 |  |  | battery vendor model
41365 | L | [5 empty] | 315 |  |  | Model Length - register value depends on the number of batteries: 109 for 1 battery, 207 for 2 batteries, 305 for 3 batteries
41366 | V_SF | Voltage Scale Factor |  | sunssf |  |  | -1 |  | R | Scale Factor for Voltage
41367 | A_SF | Current Scale Factor |  | sunssf |  |  | -1 |  | R | Scale Factor for Current
41368 | W_SF | Power Scale Factor |  | sunssf |  |  | 0 |  | R | Scale Factor for Active Power
41369 | Tmp_SF | Temperature Scale Factor |  | sunssf |  |  | -1 |  | R | Scale Factor for Temperature
41370 | SoC_SF | State of Charge (SoC) Scale Factor |  | sunssf |  |  | 0 |  | R | Scale Factor for Charging State
41371 | SoH_SF | State of Health (SoH) Scale Factor |  | sunssf |  |  | 0 |  | R | Scale Factor for Health State
41372 | WH_SF | Energy Scale Factor |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Energy
41373 | AH_SF | Charge Scale Factor |  | sunssf |  |  | 0 |  | R | Scale Factor for Charging
41374 | N | Number of Battery units |  | uint16 |  |  | supported |  | R | Number of Batteries
41375 | SoC | State Of Charge (SoC) |  | uint16 | Pct | SoC_SF | supported |  | R | State of Charge (average of battery units)
41376 | W | Total Batteries power |  | int16 | W | W_SF | supported |  | R | Sum of Batteries Powers
41377 | Mn | Manufacturer | 1 | string |  |  | supported |  | R | Manufacturer specific value
41393 | Md | Model | 1 | string |  |  | supported |  | R | Manufacturer specific value
41409 | Opt | Options | 1 | string |  |  | unimplemented |  | R | Manufacturer specific value
41417 | Vr | Version | 1 | string |  |  | supported |  | R | Manufacturer specific value
41425 | SN | Serial Number | 1 | string |  |  | supported |  | R | Manufacturer specific value
41441 | BEvt | Battery unit Events | 1 | bitfield32 |  |  | unimplemented |  | R | Manufacturer specific value
41443 | BA | Current - Battery unit | 1 | int16 | A | A_SF | supported |  | R | Current for Battery unit
41444 | BV | Voltage - Battery unit | 1 | uint16 | V | V_SF | supported |  | R | Voltage for Battery unit
41445 | BW | Power - Battery unit | 1 | int16 | W | W_SF | supported |  | R | Power for Battery unit
41446 | TmpCh | charger Temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | supported |  | R | Battery DC/DC converter temperature
41447 | BSoC | State of Charge - Battery unit | 1 | uint16 | Pct | SoC_SF | supported |  | R | State of Charge for Battery unit
41448 | VcellMax | Max cell voltage - Battery unit | 1 | uint16 | V | V_SF | supported |  | R | Max cell voltage within the Battery unit
41449 | VcellMin | Min cell voltage - Battery unit | 1 | uint16 | V | V_SF | supported |  | R | Min cell voltage within the Battery unit
41450 | TmpCellMax | Max cell temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | supported |  | R | Max cell temperature within the Battery unit
41451 | TmpCellMin | Min cell temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | supported |  | R | Min cell temperature within the Battery unit
41452 | SoH | State of Health - Battery unit | 1 | uint16 | Pct | SoH_SF | supported |  | R | State of Health for Battery unit
41453 | SHU | Last time of health check - Battery unit | 1 | uint64 | Secs |  | supported |  | R | Time since last check of Health (Unix time format)
41457 | WChMax | Max charge power (lifetime) - Battery unit | 1 | uint16 | W | W_SF | supported |  | R | Lifetime peak of charging Power for Battery unit
41458 | WDischMax | Max discharge power (lifetime) - Battery unit | 1 | uint16 | W | W_SF | supported |  | R | Lifetime peak of discharging Power for Battery unit
41459 | ChTms | Charging time (lifetime) - Battery unit | 1 | uint32 | Secs |  | unimplemented |  | R | Lifetime charging time for Battery unit
41461 | DischTms | Discharging time (lifetime) - Battery unit | 1 | uint32 | Secs |  | unimplemented |  | R | Lifetime discharging time for Battery unit
41463 | FullAH | Full charge capacity - Battery unit | 1 | uint16 | AH | AH_SF | supported |  | R | Full charge capacity for Battery unit
41464 | WHCh | Energy charged (Lifetime) - Battery unit | 1 | acc64 | WH | WH_SF | supported |  | R | Lifetime overall charged energy
41468 | WHDisch | Energy discharged (Lifetime) - Battery unit | 1 | acc64 | WH | WH_SF | supported |  | R | Lifetime overall discharged energy
41472 | Cycles | Cycle count - Battery unit | 1 | uint32 |  |  | supported |  | R | Counter for charging/discharging cycles
41474 | Pad | Pad | 1 | pad |  |  |  |  | R | Force even alignment
41475 | Mn | Manufacturer | 2 |  |  |  | supported |  | R
41491 | Md | Model | 2 |  |  |  | supported |  | R
41507 | Opt | Options | 2 |  |  |  | unimplemented |  | R
41515 | Vr | Version | 2 |  |  |  | supported |  | R
41523 | SN | Serial Number | 2 |  |  |  | supported |  | R
41539 | BEvt | Battery unit Events | 2 |  |  |  | unimplemented |  | R
41541 | BA | Current - Battery unit | 2 |  |  |  | supported |  | R
41542 | BV | Voltage - Battery unit | 2 |  |  |  | supported |  | R
41543 | BW | Power - Battery unit | 2 |  |  |  | supported |  | R
41544 | TmpCh | charger Temperature - Battery unit | 2 |  |  |  | supported |  | R
41545 | BSoC | State of Charge - Battery unit | 2 |  |  |  | supported |  | R
41546 | VcellMax | Max cell voltage - Battery unit | 2 |  |  |  | supported |  | R
41547 | VcellMin | Min cell voltage - Battery unit | 2 |  |  |  | supported |  | R
41548 | TmpCellMax | Max cell temperature - Battery unit | 2 |  |  |  | supported |  | R
41549 | TmpCellMin | Min cell temperature - Battery unit | 2 |  |  |  | supported |  | R
41550 | SoH | State of Health - Battery unit | 2 |  |  |  | supported |  | R
41551 | SHU | Last time of health check - Battery unit | 2 |  |  |  | supported |  | R
41555 | WChMax | Max charge power (lifetime) - Battery unit | 2 |  |  |  | supported |  | R
41556 | WDischMax | Max discharge power (lifetime) - Battery unit | 2 |  |  |  | supported |  | R
41557 | ChTms | Charging time (lifetime) - Battery unit | 2 |  |  |  | unimplemented |  | R
41559 | DischTms | Discharging time (lifetime) - Battery unit | 2 |  |  |  | unimplemented |  | R
41561 | FullAH | Full charge capacity - Battery unit | 2 |  |  |  | supported |  | R
41562 | WHCh | Energy charged (Lifetime) - Battery unit | 2 |  |  |  | unimplemented |  | R
41566 | WHDisch | Energy discharged (Lifetime) - Battery unit | 2 |  |  |  | unimplemented |  | R
41570 | Cycles | Cycle count - Battery unit | 2 |  |  |  | supported |  | R
41572 | Pad | Pad | 2 |  |  |  | supported |  | R
41573 | Mn | Manufacturer | 3 |  |  |  | supported |  | R
41589 | Md | Model | 3 |  |  |  | supported |  | R
41605 | Opt | Options | 3 |  |  |  | unimplemented |  | R
41613 | Vr | Version | 3 |  |  |  | supported |  | R
41621 | SN | Serial Number | 3 |  |  |  | supported |  | R
41637 | BEvt | Battery unit Events | 3 |  |  |  | unimplemented |  | R
41639 | BA | Current - Battery unit | 3 |  |  |  | supported |  | R
41640 | BV | Voltage - Battery unit | 3 |  |  |  | supported |  | R
41641 | BW | Power - Battery unit | 3 |  |  |  | supported |  | R
41642 | TmpCh | charger Temperature - Battery unit | 3 |  |  |  | supported |  | R
41643 | BSoC | State of Charge - Battery unit | 3 |  |  |  | supported |  | R
41644 | VcellMax | Max cell voltage - Battery unit | 3 |  |  |  | supported |  | R
41645 | VcellMin | Min cell voltage - Battery unit | 3 |  |  |  | supported |  | R
41646 | TmpCellMax | Max cell temperature - Battery unit | 3 |  |  |  | supported |  | R
41647 | TmpCellMin | Min cell temperature - Battery unit | 3 |  |  |  | supported |  | R
41648 | SoH | State of Health - Battery unit | 3 |  |  |  | supported |  | R
41649 | SHU | Last time of health check - Battery unit | 3 |  |  |  | supported |  | R
41653 | WChMax | Max charge power (lifetime) - Battery unit | 3 |  |  |  | supported |  | R
41654 | WDischMax | Max discharge power (lifetime) - Battery unit | 3 |  |  |  | supported |  | R
41655 | ChTms | Charging time (lifetime) - Battery unit | 3 |  |  |  | unimplemented |  | R
41657 | DischTms | Discharging time (lifetime) - Battery unit | 3 |  |  |  | unimplemented |  | R
41659 | FullAH | Full charge capacity - Battery unit | 3 |  |  |  | supported |  | R
41660 | WHCh | Energy charged (Lifetime) - Battery unit | 3 |  |  |  | unimplemented |  | R
41664 | WHDisch | Energy discharged (Lifetime) - Battery unit | 3 |  |  |  | unimplemented |  | R
41668 | Cycles | Cycle count - Battery unit | 3 |  |  |  | supported |  | R
41670 | Pad | Pad | 3 |  |  |  | supported |  | R